## The RHC Company Financial Model
Section 1: Technical Calculations
Variable | Parameter | Value | Unit | Notes
PVC | PV Installed Capacity | 2000 | kWp | Floating PV, initial scenario
- | Site Location | Gili Ketapang | - | -
GHI | Global Horizontal Irradiation (GHI) | 2118.7 | kWh/m²/year | GSA report
GTI | Global Tilted Irradiation (GTI) | 2159.7 | kWh/m²/year | Optimal tilt 12°
DNI | Direct Normal Irradiation (DNI) | 1779.9 | kWh/m²/year | For advanced/optional system planning
T | Air Temperature (Average Annual) | 26.9 | °C | -
PR | System Performance Ratio (PR) | 0.86 | - | Typical floating PV PR
TA | Optimum Tilt Angle | 12 | degrees | GSA recommendation
E | Water Surface Elevation | 1 | m | Nearly sea level
SF | Siting Factor | 1 | - | Single-site scenario
HoS | Hours of Sunlight (Effective, est.) | 6 | hours/day | Use for further simulation
PVOA | Annual PV Output | 3714684 | kWh/year | -
SY | Specific Yield | 1857.342 | kWh/kWp/year | -
PVOM | Monthly PV Output (avg) | 309557 | kWh/month | -
PVOD | Daily PV Output (avg) | 10177.2164 | kWh/day | -
AR | Area Requirement | 20000 | m² | -
| Grid Emission Factor | 0.95 | tCO₂/MWh | Latest data, PLN/IDXCarbon/IEEFA
Section 2: Hydrogen Production and Storage Calculations
Variable | Parameter Description | Value | Unit | Calculation Formula / Reference | Notes
PVOA | Annual PV Output (from Sect. 1) | 3714684 | kWh/year |  | e.g. 1,727,760
PVOD | Daily PV Output (avg) | 10177.2164 | kWh/day | PVOA / 365 | Connect from Section 1
PDL | Daytime Peak Load | 317 | kW
PNL | Nighttime Peak Load | 425 | kW
DH/NH | Daytime Hour/Nighttime Hour | 12 | hours
DCS | Daytime Consumption (avg; 70% PDL) | 2662.8 | kWh/day | Estimate: 70% * PDL * DH
NCS | Nighttime Consumption (avg; 70% PNL) | 3570 | kWh/night | Estimate: 70% * PNL * NH
SPV | Surplus PV for Hydrogen (per day) | 7514.4164 | kWh/day | PVOD - DCS | kWh for electrolysis after direct use
EE | Electrolyzer Efficiency | 65% |  |  | PEM/Alkaline efficiency
EEC | Electrolyzer Consumption | 60.6154 | kWh/kg H₂ | 39.4 / EE | Energy needed for 1 kg H₂ (LHV basis)
HPD | Hydrogen Produced per Day | 123.9688 | kg H₂/day | SPV / EEC | Daily output
HFCGE | HFCG Electrical Efficiency | 50% |  | e.g. 50% (enter as 0.5) | Fuel cell/losses
HFCGO | HFCG Energy Output per Day | 2065.94 | kWh/day | HPD × 33.33 × HFCGE | 33.33 kWh/kg H₂ (LHV basis)
NLD | Night Load Demand | 3570 | kWh/night | Demand for all night load (sum) | e.g. 2,400
NLS | Night Load Served by HFCG | 57.87% |  | HFCGO / NLD | Percentage of demand covered
H2_Storage_Req | Hydrogen Storage Requirement | 619.844 | kg | HPD × Storage Days | For backup autonomy
StoP | Storage Pressure | 300 | bar | Recommended 300–700 | Pressurized hydrogen
StoV | Storage Volume | 6896.3843 | Nm³ | H2_Storage_Req × 11.126 | 1 kg H₂ ≈ 11.126 Nm³ at STP
RV | Real Volume at StoP (litres) | 22987.9476 | litres
EPSN | Electrolyzer Plant Size Needed | 939.3021 | kW
EPSU | Electrolyzer Plant Size Used | 900 | kW
HFCG1 | Current HFCG Installed | 80 | kW
| Current HFCG Output | 960 | kWh/day
HFCG2 | Additional HFCG Needed | 96.1617 | kW
WH2 | Water Needed to Produce H2 | 1115.7192 | litres/day |  | Typically electrolyzer needed 9 litres of water for producing 1 kg of H2
INF | Inflation Rate | 2%
Tarrif | Tariff to PLN | 0.13 | USD/kWh
LR | Loan Amount Ratio | 40%
LA | Loan Amout (USD) | 1584334.8488
IR | Interest Rate (%) | 5.5%
| CAPEX for H2 System (USD) | -1643072.9339
| Rate for IaaS Loan (%) | 15%
| Service Fee for H2 System (% of CAPEX) | 5%
| Service Cost for H2 System (% of CAPEX) | 1.8%
| Carbon Trade Price (USD/tCO2) | 8 | USD/tCO2
Section 3: Financial Model & Cashflow
Year
No. | Description |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
1 | REVENUE
| Electricity Sales (Grid Offset) | [5 empty] | 482908.92 | 480494.3754 | 478091.9035 | 475701.444 | 473322.9368 | 470956.3221 | 468601.5405 | 466258.5328 | 463927.2401 | 461607.6039 | 459299.5659 | 457003.0681 | 454718.0527 | 452444.4625 | 450182.2402 | 447931.329 | 445691.6723 | 443463.214 | 441245.8979 | 439039.6684
| Build-Transfer Revenue From IaaS H2 (IaaS Loan) |  |  |  |  | Year 1: 327385.6709; Year 2: 327385.6709; Year 3: 327385.6709; Year 4: 327385.6709; Year 5: 327385.6709; Year 6: 327385.6709; Year 7: 327385.6709; Year 8: 327385.6709; Year 9: 327385.6709; Year 10: 327385.6709
| O&M Service Fee | [5 empty] | 82153.6467 | 83796.7196 | 85472.654 | 87182.1071 | 88925.7492 | 90704.2642 | 92518.3495 | 94368.7165 | 96256.0908 | 98181.2126 | 100144.8369 | 102147.7336 | 104190.6883 | 106274.5021 | 108399.9921
| Carbon Revenue | [5 empty] | 28231.5984 | 28090.4404 | 27949.9882 | 27810.2383 | 27671.1871 | 27532.8311 | 27395.167 | 27258.1911 | 27121.9002 | 26986.2907 | 26851.3592 | 26717.1024 | 26583.5169 | 26450.5993 | 26318.3463 | 26186.7546 | 26055.8208 | 25925.5417 | 25795.914 | 25666.9345
| Total Revenue | [5 empty] | 892448.2376 | 891676.766 | 890950.2285 | 890269.2221 | 889634.357 | 889046.2573 | 888505.5609 | 888012.9202 | 887569.0019 | 887174.4875 | 559444.4028 | 559150.8017 | 558908.741 | 558718.9646 | 558582.2323 | 447931.329 | 445691.6723 | 443463.214 | 441245.8979 | 439039.6684
2 | CAPITAL EXPENDITURE (CAPEX)
| PV Plant (EPC & Installation) |  |  |  |  | Year 0: -2000000
| Balance of Plant/ Infrastucture (PV) |  |  |  |  | Year 0: -200000
| Electrolyzer |  |  |  |  | Year 0: -720000
| HFCG Unit(s) |  |  |  |  | Year 0: -153858.6716
| Hydrogen Storage |  |  |  |  | Year 0: -619843.9955
| Balance of Plant/Infrastructure (H2) |  |  |  |  | Year 0: -149370.2667
| PPn (11%) |  |  |  |  | Year 0: exempted using the IPP renewable project scheme with note from Kementerian ESDM & BKPM (e.g. Cirata Project)
| Land/Sea Lease and Permitting |  |  |  |  | Year 0: -2400
| Other CAPEX |  |  |  |  | Year 0: -115364.188
| Total CAPEX |  |  |  |  | Year 0: -3960837.1219
3 | OPERATING EXPENDITURE (OPEX)
| PV O&M | [5 empty] | -30000 | -30600 | -31212 | -31836.24 | -32472.9648 | -33122.4241 | -33784.8726 | -34460.57 | -35149.7814 | -35852.7771 | -36569.8326 | -37301.2293 | -38047.2538 | -38808.1989 | -39584.3629 | -40376.0501 | -41183.5712 | -42007.2426 | -42847.3874 | -43704.3352
| Admin/Insurance/Security | [5 empty] | -33000 | -33660 | -34333.2 | -35019.864 | -35720.2613 | -36434.6665 | -37163.3598 | -37906.627 | -38664.7596 | -39438.0548 | -40226.8159 | -41031.3522 | -41851.9792 | -42689.0188 | -43542.7992 | -44413.6552 | -45301.9283 | -46207.9668 | -47132.1262 | -48074.7687
| Staff & Community Program | [5 empty] | -18000 | -18360 | -18727.2 | -19101.744 | -19483.7789 | -19873.4545 | -20270.9235 | -20676.342 | -21089.8689 | -21511.6662 | -21941.8996 | -22380.7376 | -22828.3523 | -23284.9193 | -23750.6177 | -24225.6301 | -24710.1427 | -25204.3455 | -25708.4325 | -26222.6011
| Major Replacement/Refurbishment |  |  |  |  | Year 6: -160000; Year 12: -160000
| Service Cost for H2 System | [5 empty] | -29575.3128 | -30166.8191 | -30770.1554 | -31385.5586 | -32013.2697 | -32653.5351 | -33306.6058 | -33972.7379 | -34652.1927 | -35345.2366 | -36052.1413 | -36773.1841 | -37508.6478 | -38258.8207 | -39023.9972
| Carbon Trading Certification | [5 empty] | 2823.1598 | 2809.044 | 2794.9988 | 2781.0238 | 2767.1187 | 2753.2831 | 2739.5167 | 2725.8191 | 2712.19 | 2698.6291 | 2685.1359 | 2671.7102 | 2658.3517 | 2645.0599 | 2631.8346 | 2618.6755 | 2605.5821 | 2592.5542 | 2579.5914 | 2566.6934
| Total OPEX | [5 empty] | -81000 | -82620 | -84272.4 | -85957.848 | -87677.005 | -249430.5451 | -91219.156 | -93043.5391 | -94904.4099 | -96802.4981 | -98738.548 | -260713.319 | -102727.5854 | -104782.1371 | -106877.7798 | -109015.3354 | -111195.6421 | -113419.555 | -115687.9461 | -118001.705
4 | Technical Production
| PV Output (kWh) | [5 empty] | 3714684 | 3696110.58 | 3677630.0271 | 3659241.877 | 3640945.6676 | 3622740.9392 | 3604627.2345 | 3586604.0984 | 3568671.0779 | 3550827.7225 | 3533073.5839 | 3515408.216 | 3497831.1749 | 3480342.019 | 3462940.3089 | 3445625.6074 | 3428397.4793 | 3411255.4919 | 3394199.2145 | 3377228.2184
| Daytime Consumption (kWh) | [5 empty] | 971922 | 991360.44 | 1011187.6488 | 1031411.4018 | 1052039.6298 | 1073080.4224 | 1094542.0309 | 1116432.8715 | 1138761.5289 | 1161536.7595 | 1184767.4947 | 1208462.8446 | 1232632.1015 | 1257284.7435 | 1282430.4384 | 1308079.0471 | 1334240.6281 | 1360925.4406 | 1388143.9494 | 1415906.8284
| Nighttime Consumption (kWh) | [5 empty] | 1303050 | 1329111 | 1355693.22 | 1382807.0844 | 1410463.2261 | 1438672.4906 | 1467445.9404 | 1496794.8592 | 1526730.7564 | 1557265.3715 | 1588410.679 | 1620178.8926 | 1652582.4704 | 1685634.1198 | 1719346.8022 | 1753733.7383 | 1788808.413 | 1824584.5813 | 1861076.2729 | 1898297.7984
| Surplus PV to H₂ | [5 empty] | 2742762 | 2704750.14 | 2666442.3783 | 2627830.4752 | 2588906.0378 | 2549660.5168 | 2510085.2037 | 2470171.2269 | 2429909.549 | 2389290.963 | 2348306.0892 | 2306945.3714 | 2265199.0734 | 2223057.2755 | 2180509.8706 | 2137546.5602 | 2094156.8513 | 2050330.0513 | 2006055.265 | 1961321.39
| H₂ Produced (kg) | [5 empty] | 45248.6117 | 44621.5125 | 43989.5316 | 43352.5332 | 42710.3788 | 42062.9273 | 41410.0351 | 40751.5558 | 40087.3403 | 39417.2367 | 38741.0903 | 38058.7434 | 37370.0355 | 36674.8028 | 35972.8786 | 35264.093 | 34548.2729 | 33825.242 | 33094.8204 | 32356.825
| HFCG Output (kWh) | [5 empty] | 754068.1136 | 743617.5052 | 733085.5445 | 722469.9661 | 711768.4626 | 700978.6836 | 690098.2347 | 679124.677 | 668055.5257 | 656888.2496 | 645620.2699 | 634248.9594 | 622771.6412 | 611185.5881 | 599488.0215 | 587676.1098 | 575746.9683 | 563697.6573 | 551525.1813 | 539226.488
| Usable Elec (kWh) | [5 empty] | 1725990.1136 | 1734977.9452 | 1744273.1933 | 1753881.3679 | 1763808.0924 | 1774059.106 | 1784640.2656 | 1795557.5484 | 1806817.0546 | 1818425.0091 | 1830387.7646 | 1842711.8039 | 1855403.7427 | 1868470.3316 | 1881918.4598 | 1895755.1569 | 1909987.5964 | 1924623.0979 | 1939669.1308 | 1955133.3164
| % Night Load Served | [5 empty] | 57.87% | 55.95% | 54.07% | 52.25% | 50.46% | 48.72% | 47.03% | 45.37% | 43.76% | 42.18% | 40.65% | 39.15% | 37.68% | 36.26% | 34.87% | 33.51% | 32.19% | 30.89% | 29.63% | 28.41%
| Annual CO2 Avoided (tCO2/year) | [5 empty] | 3528.9498 | 3511.3051 | 3493.7485 | 3476.2798 | 3458.8984 | 3441.6039 | 3424.3959 | 3407.2739 | 3390.2375 | 3373.2863 | 3356.4199 | 3339.6378 | 3322.9396 | 3306.3249 | 3289.7933 | 3273.3443 | 3256.9776 | 3240.6927 | 3224.4893 | 3208.3668
4 | EBITDA (Earnings before interest, tax, depreciation, amortization)
| EBITDA | [5 empty] | 811448.2376 | 809056.766 | 806677.8285 | 804311.3741 | 801957.352 | 639615.7122 | 797286.405 | 794969.3812 | 792664.592 | 790371.9895 | 460705.8548 | 298437.4827 | 456181.1557 | 453936.8275 | 451704.4525 | 338915.9936 | 334496.0302 | 330043.659 | 325557.9518 | 321037.9634
| Depreciation & Amortization | [5 empty] | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135 | -236297.3135
| EBIT (Earnings before interest and tax) | [5 empty] | 575150.9241 | 572759.4524 | 570380.515 | 568014.0605 | 565660.0385 | 403318.3987 | 560989.0915 | 558672.0676 | 556367.2785 | 554074.6759 | 224408.5413 | 62140.1692 | 219883.8422 | 217639.5139 | 215407.1389 | 102618.68 | 98198.7167 | 93746.3455 | 89260.6383 | 84740.6499
| Opening Balance | [5 empty] | 1584334.8488 | 1538897.1867 | 1490960.4533 | 1440387.1996 | 1387032.4168 | 1330743.1211 | 1271357.914 | 1208706.5206 | 1142609.3006 | 1072876.7334 | 999308.875 | 921694.7845 | 839811.9189 | 753425.4958 | 662287.8193 | 566137.5707 | 464699.0584 | 357681.4279 | 244777.8277 | 125664.5296
| Loan Repayment | [5 empty] | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787 | -132576.0787
| Interest | [5 empty] | -87138.4167 | -84639.3453 | -82002.8249 | -79221.296 | -76286.7829 | -73190.8717 | -69924.6853 | -66478.8586 | -62843.5115 | -59008.2203 | -54961.9881 | -50693.2131 | -46189.6555 | -41438.4023 | -36425.8301 | -31137.5664 | -25558.4482 | -19672.4785 | -13462.7805 | -6911.5491
| Principal | [5 empty] | 45437.662 | 47936.7334 | 50573.2538 | 53354.7827 | 56289.2958 | 59385.207 | 62651.3934 | 66097.2201 | 69732.5672 | 73567.8584 | 77614.0906 | 81882.8656 | 86386.4232 | 91137.6764 | 96150.2486 | 101438.5123 | 107017.6305 | 112903.6002 | 119113.2982 | 125664.5296
| Closing Balance | [5 empty] | 1538897.1867 | 1490960.4533 | 1440387.1996 | 1387032.4168 | 1330743.1211 | 1271357.914 | 1208706.5206 | 1142609.3006 | 1072876.7334 | 999308.875 | 921694.7845 | 839811.9189 | 753425.4958 | 662287.8193 | 566137.5707 | 464699.0584 | 357681.4279 | 244777.8277 | 125664.5296 | -9.8953e-10
| Tax | [5 empty] | -107362.7516 | -107386.4236 | -107443.0918 | -107534.4082 | -107662.1162 | -72628.0559 | -108034.1694 | -108282.506 | -108575.2287 | -108914.6202 | -37278.2417 | -2518.3303 | -38212.7211 | -38764.2446 | -39375.888 | -15725.845 | -15980.8591 | -16296.2507 | -16675.5287 | -17122.4022
5 | NET PROFIT |  |  |  |  | -3960837.1219 | 380649.7558 | 380733.6836 | 380934.5982 | 381258.3563 | 381711.1393 | 257499.4711 | 383030.2368 | 383910.703 | 384948.5382 | 386151.8354 | 132168.3114 | 8928.6257 | 135481.4656 | 137436.8671 | 139605.4209 | 55755.2686 | 56659.4094 | 57777.6162 | 59122.3291 | 60706.6986
| Free Cash Flow to Equity (FCFE) |  |  |  |  | -3960837.1219 | 571509.4073 | 569094.2637 | 566658.658 | 564200.8872 | 561719.1571 | 434411.5776 | 556676.1569 | 554110.7965 | 551513.2846 | 548881.2905 | 290851.5344 | 163343.0737 | 285392.3559 | 282596.5042 | 279752.4858 | 190614.0699 | 185939.0924 | 181171.3296 | 176306.3444 | 171339.4826
| Accumulated Cash Flow |  |  |  |  | -3960837.1219 | -3389327.7146 | -2820233.4509 | -2253574.7929 | -1689373.9058 | -1127654.7487 | -693243.1711 | -136567.0141 | 417543.7823 | 969057.0669 | 1517938.3575 | 1808789.8919 | 1972132.9656 | 2257525.3215 | 2540121.8258 | 2819874.3116 | 3010488.3814 | 3196427.4739 | 3377598.8035 | 3553905.1479 | 3725244.6304
6 | LCOE
| Total CAPEX (USD) |  |  |  |  | Year 0: -3960837.1219
| Discount Factor | [5 empty] | 0.92593 | 0.85734 | 0.79383 | 0.73503 | 0.68058 | 0.63017 | 0.58349 | 0.54027 | 0.50025 | 0.46319 | 0.42888 | 0.39711 | 0.3677 | 0.34046 | 0.31524 | 0.29189 | 0.27027 | 0.25025 | 0.23171 | 0.21455
| Discounted OPEX (USD) | [5 empty] | -75000 | -70833.3333 | -66898.1481 | -63181.5844 | -59671.4963 | -157183.5535 | -53225.5014 | -50268.5291 | -47475.833 | -44838.2867 | -42347.2708 | -103532.846 | -37772.7199 | -35674.2355 | -33692.3335 | -31820.5372 | -30052.7296 | -28383.1335 | -26806.2928 | -25317.0543
| Discounted Electricity (kWh) | [5 empty] | 1598138.994 | 1487463.9448 | 1384660.298 | 1289155.1637 | 1200418.1505 | 1117958.1649 | 1041320.454 | 970083.8738 | 903858.3654 | 842282.6228 | 785021.9382 | 731766.2106 | 682228.1056 | 636141.3549 | 593259.1839 | 553352.8591 | 516210.345 | 481635.0617 | 449444.7378 | 419470.3483
7 | IRR | 9.847%
8 | NPV | 438937.8481 | USD | (with 8% of discount rate)
9 | Payback Period | 9.7535 | years
CAPEX Category | Benchmark Value | Unit | Calculation Formula for Total | Notes / Source
PV Plant (EPC & Installation) | 1000 | USD/kWp | Installed Capacity (kWp) × Value | IEA PVPS 2025 , SERIS, Indonesia PLTS
Electrolyzer (PEM/Alkaline) | 800 | USD/kW | Electrolyzer Size (kW) × Value | Hydrogen Council, KPMG, IEA |  | Year 8: -0.24646
HFCG Unit(s) (Fuel Cell, stationary) | 1600 | USD/kW | HFCG size (kW) × Value | IEA, Hydrogen Council
Hydrogen Storage (compressed, 300 bar) | 1000 | USD/kg H₂ stored | Storage Capacity (kg) × Value | KPMG, IEA, recent projects
Balance of Plant/Infrastructure | 10% |  | (PV EPC + Electrolyzer + HFCG) × % | For site, grid, water, civil
Land/Sea Lease and Permitting | 1200 | USD/ha/year | Surface area (ha) × $1,900 | Indonesia KKP standard, 2025
Other CAPEX (Engineering/Dev, Contingency) | 3% |  | Total CAPEX × % | Industry standard
Asset Group | Depreciation Life (yr) | Annual Depreciation (USD)
PV Plant (EPC & Install) | 20 | -100000
Electrolyzer | 10 | -72000
HFCG Unit(s) | 10 | -15385.8672
Hydrogen Storage | 15 | -41322.933
Balance of Plant/Infrastructure | 20 | -7468.5133
Land/Sea Lease and Permitting | 20 | -120
Total Depreciation Each Year (USD/Year) |  | -236297.3135

## The FWC Company Financial Model
Section 1: Technical Calculations
Variable | Parameter | Value | Unit | Notes
SWROC | SWRO Installed Capacity (Nominal) | 800 | m3/day | Target average daily output for population/industry
OPSR | Operational Schedule Ratio (avail.) | 95% | percent | Uptime after maintenance/downtime
SWROP | SWRO Output per Year | 277400 | m3/year | SWROC x OPSR x 365
FEEDR | Feedwater Intake Requirement | 1454.5455 | m3/day | Typical recovery 55 percent (RO ratio)
ENE | SWRO Specific Energy Consumption | 3.1735 | kWh/m3 | Conservative, with WHR effect (~5% less than baseline)
ENEBASE | Baseline SWRO SEC (no WHR) | 3.4 | kWh/m3 | Reference for efficiency comparison
ENEYEAR | Annual Energy Use | 880319.7896 | kWh/year | SWRO Output x ENE
WHRU | WHR Utilization Temperature Gain | 2.2209 | Celsius | From HFCG, annual-averaged
PRSWRO | SWRO Plant Recovery Ratio | 55% | percent | Feedwater converted to product water
FWI | Feedwater Salinity Input | 38000 | mg/L | Sea/brackish water (East Java islands)
PROD | Product Water Salinity (output) | 500 | mg/L | Meets PDAM potable standards
MEMB | Membrane Type | SWRO Polyamide | - | High-rejection, industry standard
MEMBLIFE | Membrane Life Span | 6 | years | Typical, with cleaning
CHEM | Chemical Consumption | 2.5 | g/m3 | Antiscalants/cleaning per m3 output
CHEMYEAR | Annual Chemical Use | 693.5 | kg/year | CHEM x SWRO Output
REPL | Major Replacements Interval | 6 | years | Membrane/pump replacement
STAFF | Staffing Requirement | 8 | FTE | O&M and monitoring
TANK | Product Water Storage | 250 | m3 | Buffer stock for downtime/peak hours
PIPE | Distribution Pipe Output (Main Island) | 1000 | m | To PDAM tie-in
SITE | Siting Elevation | 2 | m | Near coastline, WHR access
GRID | Electricity Source | PLN | - | Tariff per hackathon scenario
EMI | Emissions Factor (electricity) | 0.95 | tCO2/MWh | PLN standard reference
REUSED | Brine Reuse Potential | 10% | percent | For ice/fish pond pilot use
PLN | PLN Electricity Cost | 0.09 | USD/kWh
CONV | USD to IDR | 16770 | IDR
Section 2: Clean Water Production and Storage Calculations
Variable | Parameter Description | Value | Unit | Calculation Formula / Reference
SWROP | SWRO Output per Year | 277400 | m3/year | SWROC × OPSR × 365
ENEYEAR | Annual Energy Use | 880319.7896 | kWh/year | SWROP × ENE
FEEDR | Feedwater Intake Requirement (daily) | 1454.5455 | m3/day | SWROC / PRSWRO × 100
FEEDYEAR | Annual Feedwater Requirement | 504363.6364 | m3/year | FEEDR × OPSR × 365
CHEMYEAR | Annual Chemical Use | 693.5 | kg/year | CHEM × SWROP
CHEMCOST | Annual Chemical Cost | 827.0722 | USD/year | CHEMYEAR × 20.000 idr/kg
MEMBRAIN | Number of Membrane Units | 16 | unit | Based on SWROC, manufacturer design (insert after design)
MEMBREP | Annual Membrane Replacement Cost | 2385.2117 | USD/year | (MEMBLIFE ÷ 365) × 15.000.000 IDR × MEMBRAIN
OPEXTOTAL | Total Annual OPEX (est.) | 171647.982 | IDR/year | Energy cost + CHEMCOST + MEMBREP + labor + other
ENECOST | Annual Electricity Cost | 79228.7811 | USD/year | ENEYEAR × electricity tariff (see GRID/PLN price)
LABCOST | Annual Labor Cost | 89206.9171 | USD/year | STAFF × average salary × 12
PRODUCT | Product Water Delivered (daily) | 800 | m3/day | SWROC
WHRSAVE | Energy Saved by WHR | 66147.5899 | kWh/year | (ENEBASE − ENE) × SWROP
WHRMONEY | Money Saved by WHR | 5953.2831 | IDR/year | WHRSAVE × electricity tariff
BRIYIELD | Brine Output per Day | 654.5455 | m3/day | FEEDR − SWROC
BRIYEAR | Brine Output per Year | 226963.6364 | m3/year | BRIYIELD × OPSR × 365
REUWAR | Brine Reused per Year | 22696.3636 | m3/year | BRIYEAR × REUSED ÷ 100
CAPINIT | Initial CAPEX Estimate | 1900000 | IDR/unit | Construction + equipment + buffer tanks + installation
MAJREP | Major Replacement CAPEX (every 6 yr) | 36000 | USD/6 years | For membranes, HP pumps, relayed as CAPEX in year n
CARBcUT | Annual CO2 Saving (grid offset) | 836.3038 | tCO2/year | ENEYEAR × EMI ÷ 1000
TANKBUFF | Buffer Storage Days | 0.3125 | day | TANK ÷ SWROC
SALLARY | Staff Salary for Chem Treatment | 187000000 | IDR/year
| OPEX Inflation per year | 2.5% | per year
| Rate for BLT | 16%
| Service Fee for SWRO (% of CAPEX) | 4%
| Asset Lifetime | 20 | years
| Loan Percentage (% of CAPEX) | 30%
| Loan Amount (USD) | 161713.125 | USD
| Loan Interest (%) | 7%
Section 3: Efficiency Gain from Intergration of WHR
Variable | Parameter Description | Value | Unit | Calculation Formula / Reference
HPD | Hydrogen Produced per Day | 123.9688 | kg/day | From electrolyzer/HFCG calculations
HFCG_EFF | HFCG Electrical Efficiency | 0.5 | - | Input efficiency of fuel cell generator
H_H2 | LHV of H₂ | 33.33 | kWh/kg | Lower Heating Value of H₂
HFCGO | HFCG Output (electrical) | 2065.94 | kWh/day | HPD × H_H2 × HFCG_EFF
HFCG_HEAT | Waste Heat Generated per Day | 2065.94 | kWh/day | HPD × H_H2 × (1 − HFCG_EFF)
WATERMASS | Water to be pre-heated (SWRO feed) | 800000 | kg/day | SWROC × 1.000 (density, 1 m³ = 1.000 kg)
C_WATER | Specific Heat of Water | 4.186 | kJ/kg·°C | Use for temp rise calculation
H_HEAT | Waste Heat in kJ/day | 7437384.1338 | kJ/day | HFCG_HEAT × 3.6 (kWh to kJ)
DELTAT | Temp. Rise in Preheated Feedwater | 2.2209 | °C | H_HEAT / (WATERMASS × C_WATER)
EFF_GAIN | SWRO Efficiency Gain per °C | 3 | %/°C | Industry reference |  |  | Total Cost for PDAM (USD) |  | 112480.6596 | USD/year
PGAIN | Projected Efficiency Gain | 6.663% | % | DELTAT × EFF_GAIN |  |  | Total Cost for PDAM (Rp) |  | 1886300662.1166 | Rp/year
ENEBASE | Baseline SWRO SEC (no WHR) | 3.4 | kWh/m³ | Reference |  |  | Production Cost/m3 (Rp/m3) |  | 6799.9303 | Rp/m3
ENE_NEW | New SWRO SEC (with WHR) | 3.1735 | kWh/m³ | ENEBASE × (1 − PGAIN / 100)
E_SAVE | Daily Energy Saved | 181.2263 | kWh/day | (ENEBASE − ENE_NEW) × SWROC
ANNUAL_SAVE | Annual Energy Saved | 66147.5899 | kWh/year | E_SAVE × 365
Section 3: Financial Model & Cashflow
Year
No. | Description |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
1 | REVENUE
| Lease/BLT Payment from PDAM |  |  |  |  | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096 | 90918.9096
| O&M Service Fee |  |  |  |  | 21561.75 | 22100.7937 | 22653.3136 | 23219.6464 | 23800.1376 | 24395.141 | 25005.0196 | 25630.145 | 26270.8987 | 26927.6711 | 27600.8629 | 28290.8845 | 28998.1566 | 29723.1105 | 30466.1883 | 31227.843 | 32008.5391 | 32808.7525 | 33628.9714 | 34469.6956
| Total Revenue |  |  |  |  | 112480.6596 | 113019.7034 | 113572.2232 | 114138.5561 | 114719.0472 | 115314.0507 | 115923.9292 | 116549.0547 | 117189.8083 | 117846.5808 | 118519.7726 | 119209.7941 | 119917.0662 | 120642.0202 | 121385.0979 | 122146.7526 | 122927.4487 | 123727.6622 | 124547.881 | 125388.6053
2 | CAPITAL EXPENDITURE (CAPEX)
| SWRO EPC & Installation |  |  |  | Year 0: -400000
| Balance of Plant (site, pipeline, tanks) |  |  |  | Year 0: -60000
| Land/Sea Lease and Permitting |  |  |  | Year 0: -2500
| Other CAPEX |  |  |  | Year 0: -23125
| Tax for CAPEX (PPn 11%) |  |  |  | Year 0: -53418.75
| Total CAPEX |  |  |  | Year 0: -539043.75
3 | OPERATING EXPENDITURE (OPEX)
| Annual O&M Service Cost |  |  |  |  | -5390.4375 | -5525.1984 | -5663.3284 | -5804.9116 | -5950.0344 | -6098.7853 | -6251.2549 | -6407.5363 | -6567.7247 | -6731.9178 | -6900.2157 | -7072.7211 | -7249.5392 | -7430.7776 | -7616.5471 | -7806.9607 | -8002.1348 | -8202.1881 | -8407.2428 | -8617.4239
| Insurance/Security/Asset Management |  |  |  |  | -1078.0875 | -1105.0397 | -1132.6657 | -1160.9823 | -1190.0069 | -1219.7571 | -1250.251 | -1281.5073 | -1313.5449 | -1346.3836 | -1380.0431 | -1414.5442 | -1449.9078 | -1486.1555 | -1523.3094 | -1561.3921 | -1600.427 | -1640.4376 | -1681.4486 | -1723.4848
| Warranty Reserves or Performance Guarantee |  |  |  |  | -5390.4375 | -5525.1984 | -5663.3284 | -5804.9116 | -5950.0344 | -6098.7853 | -6251.2549 | -6407.5363 | -6567.7247 | -6731.9178 | -6900.2157 | -7072.7211 | -7249.5392 | -7430.7776 | -7616.5471 | -7806.9607 | -8002.1348 | -8202.1881 | -8407.2428 | -8617.4239
| Major Replacement/Refurbishment |  |  |  | Year 7: -36000; Year 14: -42792.6871
| Admin/Legal Compliance |  |  |  |  | -1078.0875 | -1105.0397 | -1132.6657 | -1160.9823 | -1190.0069 | -1219.7571 | -1250.251 | -1281.5073 | -1313.5449 | -1346.3836 | -1380.0431 | -1414.5442 | -1449.9078 | -1486.1555 | -1523.3094 | -1561.3921 | -1600.427 | -1640.4376 | -1681.4486 | -1723.4848
| Total OPEX |  |  |  |  | -12937.05 | -13260.4762 | -13591.9882 | -13931.7879 | -14280.0826 | -14637.0846 | -51003.0117 | -15378.087 | -15762.5392 | -16156.6027 | -16560.5178 | -16974.5307 | -17398.894 | -60626.5534 | -18279.713 | -18736.7058 | -19205.1234 | -19685.2515 | -20177.3828 | -20681.8174
4 | Technical Production
| Water output (m3) |  |  |  |  | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400 | 277400
| Brine output (m3) |  |  |  |  | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364 | 226963.6364
| Annual CO2 avoided |  |  |  |  | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038 | 836.3038
4 | EBITDA (Earnings before interest, tax, depreciation, amortization)
| EBITDA |  |  |  |  | 99543.6096 | 99759.2271 | 99980.2351 | 100206.7682 | 100438.9647 | 100676.9661 | 64920.9175 | 101170.9677 | 101427.2691 | 101689.9781 | 101959.2548 | 102235.2634 | 102518.1723 | 60015.4667 | 103105.385 | 103410.0468 | 103722.3253 | 104042.4107 | 104370.4982 | 104706.7879
| Depreciation & Amortization |  |  |  |  | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875 | -26952.1875
| EBIT (Earnings before interest and tax) |  |  |  |  | 72591.4221 | 72807.0396 | 73028.0476 | 73254.5807 | 73486.7772 | 73724.7786 | 37968.73 | 74218.7802 | 74475.0816 | 74737.7906 | 75007.0673 | 75283.0759 | 75565.9848 | 33063.2792 | 76153.1975 | 76457.8593 | 76770.1378 | 77090.2232 | 77418.3107 | 77754.6004
| Opening Balance |  |  |  |  | 161713.125 | 157768.4688 | 153547.6866 | 149031.4496 | 144199.0761 | 139028.4364 | 133495.852 | 127575.9866 | 121241.7307 | 114464.0768 | 107211.9872 | 99452.2513 | 91149.3339 | 82265.2123 | 72759.2021 | 62587.7713 | 51704.3403 | 40059.0691 | 27598.6289 | 14265.9579
| Loan Repayment |  |  |  |  | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575 | -15264.575
| Interest |  |  |  |  | -11319.9188 | -11043.7928 | -10748.3381 | -10432.2015 | -10093.9353 | -9731.9905 | -9344.7096 | -8930.3191 | -8486.9211 | -8012.4854 | -7504.8391 | -6961.6576 | -6380.4534 | -5758.5649 | -5093.1441 | -4381.144 | -3619.3038 | -2804.1348 | -1931.904 | -998.6171
| Principal |  |  |  |  | 3944.6562 | 4220.7822 | 4516.2369 | 4832.3735 | 5170.6397 | 5532.5845 | 5919.8654 | 6334.2559 | 6777.6539 | 7252.0896 | 7759.7359 | 8302.9174 | 8884.1216 | 9506.0101 | 10171.4309 | 10883.431 | 11645.2712 | 12460.4402 | 13332.671 | 14265.9579
| Closing Balance |  |  |  |  | 157768.4688 | 153547.6866 | 149031.4496 | 144199.0761 | 139028.4364 | 133495.852 | 127575.9866 | 121241.7307 | 114464.0768 | 107211.9872 | 99452.2513 | 91149.3339 | 82265.2123 | 72759.2021 | 62587.7713 | 51704.3403 | 40059.0691 | 27598.6289 | 14265.9579 | 2.9104e-11
| Tax |  |  |  |  | -13479.7307 | -13587.9143 | -13701.5361 | -13820.9234 | -13946.4252 | -14078.4134 | -6297.2845 | -14363.4614 | -14517.3953 | -14679.5671 | -14850.4902 | -15030.712 | -15220.8169 | -6007.0372 | -15633.2117 | -15856.8774 | -16093.1835 | -16342.9394 | -16607.0095 | -16886.3163
5 | NET PROFIT |  |  |  | -539043.75 | 47791.7726 | 48175.3325 | 48578.1734 | 49001.4558 | 49446.4166 | 49914.3746 | 22326.7359 | 50924.9997 | 51470.7652 | 52045.7381 | 52651.738 | 53290.7063 | 53964.7145 | 21297.6772 | 55426.8416 | 56219.838 | 57057.6505 | 57943.1489 | 58879.3972 | 59869.667
| Free Cash Flow to Equity (FCFE) |  |  |  | -539043.75 | 70799.3039 | 70906.7378 | 71014.124 | 71121.2698 | 71227.9645 | 71333.9777 | 43359.058 | 71542.9312 | 71645.2988 | 71745.8359 | 71844.1896 | 71939.9764 | 72032.7804 | 38743.8546 | 72207.5982 | 72288.5945 | 72364.5668 | 72434.8962 | 72498.9137 | 72555.8966
| Accumulated Cash Flow |  |  |  | -539043.75 | -468244.4461 | -397337.7083 | -326323.5843 | -255202.3145 | -183974.35 | -112640.3724 | -69281.3144 | 2261.6169 | 73906.9157 | 145652.7516 | 217496.9412 | 289436.9176 | 361469.698 | 400213.5525 | 472421.1508 | 544709.7452 | 617074.312 | 689509.2082 | 762008.122 | 834564.0185
6 | IRR | 11.25% | bar: Year 0 to Year 15
7 | NPV | 135377.2231 | USD | (with 8% of discount rate) | bar: Year 0 to Year 15
8 | Payback Period | 7.3573 | years | bar: Year 0 to Year 15
7.9684
OPERATING EXPENDITURE (OPEX)
Electricity Cost
Chemicals
Membrane/HP Pump Minor Replacement
Labor/Admin
Insurance, Security
Major Replacement (year 6/12)
O&M Fee (if paid to FWC)
Total OPEX